## Sheet1
WORKSHEET 4-1
ERU Capacity Summary
Specific Single-Family Residential Connection Criteria (measured or estimated demands)
Average Day Demand (ADD): | 164 | gpd/ERU | Ref. TM Equivalent Residential Units pg. 6
Maximum Day Demand (MDD): | 350 | gpd/ERU | MDD not less than 350 gpd/ERU
Water System Connections Correlated to ERUs
Service Classification | Total MDD for the classification, gpd | Total # Connections in the classification | ERUs
Residential
Single-family | 138950 | 397 | 397 | Ref. TM Historical Use Summary pg. 5
Multifamily
Nonresidential
Industrial
Commercial | 2800 | 10 | 8 | Ref. TM Historical Use Summary pg. 5
Governmental
Agricultural
Recreational
Other (specify)
DSL | 7582.7589 | N/A | 46 | Ref. TM Distribution System Leakage (DSL) pg. 6
Other (identify)
Total existing ERUs (Residential + Nonresidential + DSL + Other) = 451
Service Capacity as ERUs and Gallons Per Day
Water System Component (Facility) | ERU Capacity for Each Component | GPD Capacity for Each Component
Source(s)1 | 1317 | 216150 | Ref. SWSMP pg. 9; TM System Capacity pg. 12
Treatment2 | 1987 | 325920 | Ref. TM System Capacity pgs. 11 & 12
Equalizing Storage3 | 121 | 19874 | Ref. TM Total Storage pg. 17
Standby Storage3 | 780 | 128000 | Ref. TM Total Storage pg. 17
Transmission | 995 | 348480 | Ref. TM Total Storage pg. 20
Water Rights (Qa) | 1676 | 288381.2717 | Ref. TM System Capacity pg. 12; Water Rights Self-Assessment
Water Rights (Qi) | 1538 | 538272 | Ref. TM System Capacity pg. 11; Water Rights Self-Assessment
Other (specify)
Water System Service Capacity (ERUs) = 780
(based on the limiting water system component shown above)
Notes:
1) Sandy Shores Pump runing 12 hours, Dockton Springs = 85 gpm, Emergency Wells at Dockton Springs = 15 gpm
2) Dockton Springs 143 gpm; Sandy Shores 120,000 per day
3) The Storage Analysis in the TM shows storage capacity exceeding required storage for the projected 20-year demand.

## Sheet2
Specific Single-Family Residential Connection Criteria (measured or estimated demands)
Average Day Demand (ADD): | 189 | gpd/ERU Maximum Day Demand (MDD) |  | 378 | gpd/ERU
Water System Connections Correlated to ERUs
Service Classification | Total MDD for the classification, gpd | Total # Connections in the classification | ERUs
Residential
Single-family | MDD*ERUs = 57,456 | 152 | 152
Multifamily
Nonresidential
Industrial
Commercial
Governmental
Agricultural | 1,890 (MDD*ERUs) | 1 | 5
Recreational
Other (specify)
DSL | 1,512 = (DSL/MDD) | N/A | 4 = (DSL/ADD)
Other (identify)
Total existing ERUs (Residential + Nonresidential + DSL + Other) = 161
Service Capacity as ERUs and Gallons Per Day
Water System Component (Facility) | ERU Capacity for Each Component | GPD Capacity for Each Component
Source(s)
Treatment
Equalizing Storage
Standby Storage
Transmission
Water Rights (Qa and Qi)
Other (specify)
Water System Service Capacity (ERUs) =
(based on the limiting water system component shown above)
Notes:
· Capacity determinations are only for existing facilities that are operational for the water system.
· Not shown above are distribution system limitations (Section 4.5.4) on ERUs because these are location-specific within the distribution system. These limits not expected to limit the ERU capacity of the entire water system.